## Sheet2
issue | root1 | root2 | root3 | root4 | root5 | root6 | root7 | root8 | root9 | root10 | root11 | root12 | root13 | root14 | root15 | root16 | root17 | root18 | root19 | root20
Alarm on M52 Controller | Low Air Flow | Air Flow is present | Air Filter Cleanliness | Cleansable air filters | Cleanse air filters
Alarm on M52 Controller | Low Air Flow | Air Flow is present | Air Filter Cleanliness | Disposible air filters | Replace air filters
Alarm on M52 Controller | Low Air Flow | Air Flow is present | Check belt | Loose belt? | Tighten the belt
Alarm on M52 Controller | Low Air Flow | Air Flow is present | Check belt | Damaged belt? | Replace belt
Alarm on M52 Controller | Low Air Flow | Air Flow is present | Any air flow obstruction? | Yes | Eliminate the obstruction
Alarm on M52 Controller | Low Air Flow | Air Flow is present | Any air flow obstruction? | No | Check the other steps
Alarm on M52 Controller | Low Air Flow | Air Flow is present | Air deferential switch | Change by-pass switch to test only | Still showing alarm? | Yes | Check the other steps
Alarm on M52 Controller | Low Air Flow | Air Flow is present | Air deferential switch | Change by-pass switch to test only | Still showing alarm? | No | Replace air deferential switch
Alarm on M52 Controller | Low Air Flow | Air Flow is present | Wire connections are loose? | Yes | Fix loose connections
Alarm on M52 Controller | Low Air Flow | Air Flow is present | Wire connections are loose? | No | Replace PCB
Alarm on M52 Controller | Low Air Flow | Air Flow is present | Still not working after checking above steps? | Contact ClimateWorx representative
Alarm on M52 Controller | Low Air Flow | Air Flow is not present | Fan motor is running | Are belts broken? | Replace Belts
Alarm on M52 Controller | Low Air Flow | Air Flow is not present | Fan motor is running | Is blower wheel ceased? | Yes | Try aligning the blower wheel, still not working? | Replace blower
Alarm on M52 Controller | Low Air Flow | Air Flow is not present | Fan motor is not running | Is the power supply present? | No | Check the main disconnect/fuses
Alarm on M52 Controller | Low Air Flow | Air Flow is not present | Fan motor is not running | Is the power supply present? | Yes | Is overcurrent protective device tripped? | Yes | Replace overcurrent protective device
Alarm on M52 Controller | Low Air Flow | Air Flow is not present | Fan motor is not running | Is the power supply present? | Yes | Is overcurrent protective device tripped? | No | Check other motor components
Alarm on M52 Controller | Low Air Flow | Air Flow is not present | Fan motor is not running | Is the power supply present? | Yes | Is motor winding/resistance okay? | Yes | Check the fuses
Alarm on M52 Controller | Low Air Flow | Air Flow is not present | Fan motor is not running | Is the power supply present? | Yes | Is motor winding/resistance okay? | No | Replace motor
Alarm on M52 Controller | Low Air Flow | Air Flow is not present | Fan motor is not running | Is the power supply present? | Yes | Is the motor grounded properly? | Yes | Replace the motor
Alarm on M52 Controller | Low Air Flow | Air Flow is not present | Fan motor is not running | Is the power supply present? | Yes | Is the motor grounded properly? | No | Check the other steps
Alarm on M52 Controller | Low Air Flow | Air Flow is not present | Fan motor is not running | Is the power supply present? | Yes | Are motor bearings okay? | No | Replace motor
Alarm on M52 Controller | Low Air Flow | Air Flow is not present | Fan motor is not running | Is the power supply present? | Yes | Are motor bearings okay? | Yes | Contact ClimateWorx representative
Alarm on M52 Controller | High Temperature Alarm | Main temp too high | No | Check the temp high limit and adjust if necessary
Alarm on M52 Controller | High Temperature Alarm | Main temp too high | Yes | Abnormal site condition? | Check doors or other openings for air leak | Close/seal them
Alarm on M52 Controller | High Temperature Alarm | Main temp too high | Yes | Abnormal site condition? | Check if any heat load added to the space/room | No | Check the other steps
Alarm on M52 Controller | High Temperature Alarm | Main temp too high | Yes | Abnormal site condition? | Check if any heat load added to the space/room | Yes | Contact ClimateWorx representative
Alarm on M52 Controller | High Temperature Alarm | Main temp too high | Yes | Inoperative cooling system | Air flow is not present | Follow the "Low Air Flow" alarm steps
Alarm on M52 Controller | High Temperature Alarm | Main temp too high | Yes | Inoperative cooling system | Air flow is present | Check the cooling system | Air cooled (DX) | Refer the document (N/…..)
Alarm on M52 Controller | High Temperature Alarm | Main temp too high | Yes | Inoperative cooling system | Air flow is present | Check the cooling system | Chill Water (CW) | Is the water valve operational? | Yes | Check the other steps
Alarm on M52 Controller | High Temperature Alarm | Main temp too high | Yes | Inoperative cooling system | Air flow is present | Check the cooling system | Chill Water (CW) | Is the water valve operational? | No | Check control (240V AC) and analog (0-10V DC) | Is the signal present? | Yes | Check the water in line | Yes | Check the water temp or pressure drop according to the factory specifications
Alarm on M52 Controller | High Temperature Alarm | Main temp too high | Yes | Inoperative cooling system | Air flow is present | Check the cooling system | Chill Water (CW) | Is the water valve operational? | No | Check control (240V AC) and analog (0-10V DC) | Is the signal present? | Yes | Check the water in line | No | Contact the Building Management for the incoming water
Alarm on M52 Controller | High Temperature Alarm | Main temp too high | Yes | Inoperative cooling system | Air flow is present | Check the cooling system | Chill Water (CW) | Is the water valve operational? | No | Check control (240V AC) and analog (0-10V DC) | Is the signal present? | No | Check the AC signal on the transformer | Check DC signal on the main board | Both signals present? | Check wires
Alarm on M52 Controller | High Temperature Alarm | Main temp too high | Yes | Inoperative cooling system | Air flow is present | Check the cooling system | Chill Water (CW) | Is the water valve operational? | No | Check control (240V AC) and analog (0-10V DC) | Is the signal present? | No | Check the AC signal on the transformer | Check DC signal on the main board | Signals not present? | Replace the PC Board
Alarm on M52 Controller | High Temperature Alarm | Still not working after checking above steps? | Contact ClimateWorx representative
Coil | Frozen coil